| This document shall be completed in accordance with MNL-352147, Fire Prevention Program Manual, Section 16.3 and present during operations involving the use of flame, heat, or sparking tools (Including but not limited to torches, heat irons, cutters, grinders, and welding equipment). Department of Energy (DOE) requires Hot Work permit required for operations in excess of 226 degrees in certain areas. (DOE Order 1212) Permit is only valid for 24 hours after signed by Permit Authorizing Individual. |  |  |  | Emergency Numbers |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Emergency | 806-477-3333 |  |  |  |
|  |  |  |  | EOC | 806-477-5000 |  |  |  |
|  |  |  |  | Fire Inspectors | 806-477-6833 806-477-5855 |  |  |  |
| Date: |  | Building / Location of Hot Work: | Building Manager Contacted, Date / Time | Safety | 806-477-6212 806-477-3556 806-477-5810 |  |  |  |
| Pantex Trades | Description and type of Hot Work: |  |  |  |  |  |  |  |
| Contractor |  |  |  | PSTR/Supervisor |  |  |  |  |
| PRECAUTIONS BEFORE OPERATIONS |  |  |  |  |  |  | Safe | N/A |
| Fire extinguishers - Pressure is indicating green/good, all parts are present, in reasonable good shape, Inspection tag is present and stamped within 1 year. (Contractors) Two 20 pound 4A:20 BC rated readily accessible, (Pantex) Minimum, UL 299 UL, 10 pound ABC or BC rated Amerex Model 419 or 441 dry chemical fire extinguisher readily accessible. |  |  |  |  |  |  |  |  |
| Inspect facility for the presence of explosives and hazardous conditions, before, during and after Hot Work operation. |  |  |  |  |  |  |  |  |
| Proper personal protective equipment on hand. |  |  |  |  |  |  |  |  |
| Sprinkler heads are protected with fire restraint non-combustible material. |  |  |  |  |  |  |  |  |
| Are Smoke and fire detection system placed out of service? |  |  |  |  |  |  |  |  |
| Everyone knows the location of a phone and emergency phone numbers. |  |  |  |  |  |  |  |  |
| Adequate ingress or egress. Pedestrian traffic is protected. |  |  |  |  |  |  |  |  |
| Equipment being used is in good working order and does not pose a hazard. Compressed Cylinders are secured upright. |  |  |  |  |  |  |  |  |
| Check weather for wind speed. If greater than 15 miles per hour (MPH), contact Fire Inspector for further instruction. |  |  |  |  |  |  |  |  |
| Notify Pantex Fire Department Dispatch at x7680 prior to doing any Hot Work. |  |  |  |  |  |  |  |  |
| DO NOT PERFORM HOT WORK UNTIL THE FOLLOWING ACTIONS ARE TAKEN AND MAINTAINED. IF CONDITIONS CHANGE DURING THE HOT WORK OPERATION, THIS PERMIT IS VOID AND A NEW PERMIT SHALL BE ISSUED. |  |  |  |  |  | YES | N/A | Verified |
| Flammable and combustible material is removed in all directions 35 ft. If removal is not possible, cover with fire retardant material. |  |  |  |  |  |  |  |  |
| Ensure flammable/combustible material on the other side of walls, partitions, ceilings, or roofs are removed. |  |  |  |  |  |  |  |  |
| Openings or cracks in walls, floors, ventilation ducts within 35 ft of work area are protected with fire retardant material. |  |  |  |  |  |  |  |  |
| Area is clean and any oil deposits are cleaned with 35 ft. |  |  |  |  |  |  |  |  |
| IF Ultraviolet (UV) detector/deluge system is NOT impaired, move out of area, Shut doors, prevent activation. |  |  |  |  |  |  |  |  |
| If floor is combustible, wet down area or protect area with fire retardant material as necessary. |  |  |  |  |  |  |  |  |
| Be aware of special requirements below. |  |  |  |  |  |  |  |  |
| Additional Fire Watches are necessary? How Many? Locations: |  |  |  |  |  |  |  |  |
| POST HOT WORK FIRE WATCH |  |  |  |  |  | Completed |  |  |
| Monitor the Hot Work area for one hour after job is complete. |  |  |  |  |  |  |  |  |
| Inspect the area for hot spots. |  |  |  |  |  |  |  |  |
| Start Time End Time Completed By: |  |  |  |  |  | <<<<<<<< |  |  |
| Notify Pantex Fire Department Dispatch at x7680 before beginning and upon completion of fire watch. |  |  |  |  |  |  |  |  |
| SPECIAL REQUIREMENTS |  |  |  |  |  |  |  |  |
| Signature (Supervisor / Superintendent) Print Name Badge # Date / Time |  |  |  |  |  |  |  |  |
| HOT WORK PERMIT IS ONLY VALID WHEN BOTH SIGNATURES BELOW ARE PRESENT. |  |  |  |  |  |  |  |  |
| Signature (Fire Inspector / PAI) Print Name Badge # Date / Time |  |  |  |  |  |  |  |  |
| WELDING / BURNING / HOT WORK MAY ONLY BEGIN AFTER IT HAS BEEN VERIFIED THAT THE ABOVE CONDITIONS HAVE BEEN MET. |  |  |  |  |  |  |  |  |
| Signature (Hot Work Operator) Print Name Badge # Date / Time |  |  |  |  |  |  |  |  |